### Geotechnical Investigation Report

## Project: Transmission line

Client: --------------------------------------

Consultant: Planeteye Infra AI

Table of Contents

- SOIL TEST SUMMARY

- ENGINEERING ANALYSIS

- PILE FOUNDATION ANALYSIS AND DESIGN

- CALIFORNIA BEARING RATIO

- EARTH RESISTIVITY

# 1.SOIL TEST SUMMARY

Location 1 –: 23°26'45.97"N 69°35'58.23"E

| Depth (m) | Gravel % | Sand % | Silt % | Clay % | LL (%) | PL (%) | PI (%) | Soil Class | MDD (g/cc) | OMC (%) | Dry Density (g/cc) | FSI (%) | Bulk Density (g/cc) | UCS (kg/cm²) | SG | SBC (T/m²) | CBR (%) | Remarks | Ground Water Table (m) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0.0–0.5 | 4 | 30 | 38 | 28 | 44 | 23 | 21 | CI | 1.71 | 18 | 1.61 | 48 | 1.89 | 1.3 | 2.7 | 10 | 4 | Silty clay, medium stiff | Not encountered up to 2.0 |
| 0.5–1.0 | 8 | 34 | 35 | 23 | 41 | 22 | 19 | CL | 1.74 | 17 | 1.65 | 42 | 1.91 | 1.45 | 2.7 | 13 | 6 | Clayey silt, stiff | Not encountered up to 2.0 |
| 1.0–1.5 | 18 | 43 | 25 | 14 | 34 | 20 | 14 | CL–ML | 1.8 | 15 | 1.7 | 24 | 1.95 | 1.82 | 2.7 | 16 | 10 | Sandy clay with increasing density | Not encountered up to 2.0 |
| 1.5–2.0 | 30 | 50 | 14 | 6 | 28 | 17 | 11 | SM | 1.88 | 12 | 1.78 | 10 | 2 | 2.3 | 2.7 | 20 | 15 | Dense sandy murum, suitable founding stratum | Not encountered up to 2.0 |

| Depth (m) | Gravel % | Sand % | Silt % | Clay % | LL (%) | PL (%) | PI (%) | Soil Class | MDD (g/cc) | OMC (%) | Dry Density (g/cc) | FSI (%) | Bulk Density (g/cc) | UCS (kg/cm²) | SG | SBC (T/m²) | CBR (%) | Remarks | Ground Water Table (m) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0–1 | 6 | 32 | 36 | 26 | 43 | 23 | 20 | CI | 1.72 | 18 | 1.63 | 45 | 1.9 | 1.38 | 2.7 | 12 | 5 | Brown silty clay, medium stiff | Not encountered up to 2.0 |
| 1–2 | 24 | 47 | 20 | 9 | 31 | 18 | 13 | SM | 1.86 | 13 | 1.76 | 15 | 1.99 | 2.1 | 2.7 | 20 | 14 | Dense sandy murum with gravel, suitable founding layer | Not encountered up to 2.0 |

# 2.ENGINEERING ANALYSIS

2.1 Foundation Design Parameters:

| Parameter | Value / Assumption | Reference |
| --- | --- | --- |
| Foundation Type | 1.0 m × 1.0 m Isolated Stub Foundation | IS 6403 : 1981 |
| Depth of Foundation (Df) | 1.50 m | Site Condition |
| Allowable Settlement | 25 mm | IS 8009 (Part-1) |
| Factor of Safety | 0.3 | IS 6403 |
| Water Table | Not encountered up to 2.0 m | Preliminary Assessment |

2.2 Adopted Soil Parameters (at 1.5 m depth – Murrum / Mixed Strata):

| Borehole | c (T/m²) | φ (°) | γ (T/m³) |
| --- | --- | --- | --- |
| BH-1 | 1.50 | 20 | 1.90 |

2.4 SBC CALCULATION – DETAILED SAMPLE (BH-1):

Using:

φ = 20°
c = 1.5T/m²
γ = 1.90 T/m³
Df = 1.5m
B =  1.0m

Surcharge (q):

Cohesion Component:

Surcharge Component:

Unit Weight Term:

Ultimate Bearing Capacity:

Net Safe Bearing Capacity:

Adopted SBC :

Considering variability of near-surface silty clay, seasonal moisture fluctuations, and the requirement for conservative transmission line foundation design, the recommended design value is  20 T/m² at 1.5 m depth

2.5 SBC Values for All Locations:

| Borehole | φ (°) | c (T/m²) | γ (T/m³) | SBC (T/m²) |
| --- | --- | --- | --- | --- |
| BH-1 | 20 | 1.5 | 1.90 | 20 |

2.6 SBC Variation with Depth:

| Depth (m) | SBC (T/m²) |
| --- | --- |
| 0.5 | 10 |
| 1 | 15 |
| 1.5 (Design) | 20 |
| 2.0 | 24 |
| 3.0+ (weathered rock) | 30 |

2.7 Settlement Check

Using:

Assumptions:

q = 20T/m² = 2.0 kg/cm²
B = 100 cm
µ = 0.30
E = 180 kg/cm²
If = 1.12

Estimated Settlement:

| Borehole | Settlement (mm) | Allowable (mm) | Status |
| --- | --- | --- | --- |
| BH-1 | 11.3 | 25 | Safe |

2.8 Final Recommended SBC for Design

To maintain conservatism and uniformity across substation structures:

Net Safe Bearing Capacity = 20 T/m² at 1.5 m depth

This accounts for:

   Near-surface CI–CL soil.

   Intermediate CL–ML mixed strata.

   Dense sandy murum below 1.5 m.

   Seasonal moisture variations in the Kutch region.

   Conservative design requirements for transmission line tower foundations.

# 3. PILE FOUNDATION ANALYSIS & DESIGN

3.1 Design Parameters:

| Parameter | Value |
| --- | --- |
| Pile Type | Cast-in-situ RCC pile |
| Pile Diameters | 300&350 mm |
| Pile Depths | 1.0 m, 1.5 m, 2.0 m |
| Factor of Safety | 2.5 (Compression), 3.0 (Uplift) |
| Design Standards | IS 2911 (Part 1), IS 6403 |

3.2 Adopted Soil Parameters (Layer-wise):

| Layer | Depth (m) | Soil Type | c (T/m²) | φ (°) | γ (T/m³) |
| --- | --- | --- | --- | --- | --- |
| I | 0–1 | Medium Stiff Silty Clay (CI–CL) | 1.50 | 20 | 1.90 |
| II | 1–2 | Dense Sandy Murum (SM) | 0.50 | 32 | 2.00 |

3.3 Cross-Sectional Area of Piles:

For 300 mm pile:

For 350 mm pile:

3.4 VERTICAL LOAD CAPACITY (Detailed – 300 mm, 2.0 m Depth):

Step 1: End Bearing Capacity:

For Dense Murum Layer

Nq = 24

Effective Overburden Pressure

Step 2: Skin Friction:

Where

Ki = 1.0

δ = 0.75φ = 24°

σv = 3.80 T/m²

Step 3: Ultimate Capacity:

Step 4: Safe Compression Capacity:

Factor of Safety = 2.5

Safe Vertical Capacity (300 mm, 2.0 m) = 300 mm × 2.0 m = 3.9 T

3.5 Summary – Vertical Capacity

| Diameter | Depth | Safe Capacity (T) |
| --- | --- | --- |
| 300 mm | 1.0 m | 2.1 |
| 300 mm | 1.5 m | 3.0 |
| 300 mm | 2.0 m | 3.9 |
| 350 mm | 1.0 m | 2.8 |
| 350 mm | 1.5 m | 4.0 |
| 350 mm | 2.0 m | 5.2 |

3.6 UPLIFT CAPACITY (Sample – 350 mm, 2.0 m):

Q uplift = Qs

Using updated Qs = 3.60 T

Safe uplift capacity:     Q safe = 3.60/ 3   Safe = 1.20 T

3.7 UPLIFT LOAD CAPACITY:

| Diameter | Depth | Lateral Capacity (T) |
| --- | --- | --- |
| 300 mm | 2.0 m | 1.05 |
| 350 mm | 2.0 m | 1.20 |

3.8 LATERAL LOAD CAPACITY:

| Diameter | Depth | Lateral Capacity (T) |
| --- | --- | --- |
| 300 mm | 2.0 m | 2.4 |
| 350 mm | 2.0 m | 3.0 |

3.9 Governing Design Condition for Transmission Line /Tower Foundation

Transmission line tower foundations are generally governed by:

- Vertical compression from dead load and conductor loads.

- Uplift due to wind loading and conductor imbalance.

- Lateral loads from wind acting on the tower.

- Overturning moments generated under extreme loading conditions.

Soil Behaviour

Upper Layer (0–1 m)

- Medium stiff CI–CL silty clay.

- Moderate compressibility.

- Slight reduction in strength during monsoon due to moisture ingress.

Lower Layer (1–2 m)

- Dense sandy murum (SM).

- High bearing capacity.

- Good shaft friction and end bearing characteristics.

- Suitable founding layer for shallow piles and stub foundations.

Final Recommended Pile Configuration for Solar Plant:

300 mm Diameter Pile – 2.0 m Depth

Suitable for normal suspension tower locations where uplift demand is relatively low.

350 mm Diameter Pile – 2.0 m Depth

Recommended for angle towers, tension towers, terminal towers, and locations subjected to higher uplift and lateral forces.

Minimum Embedment Depth

2.0 m

This depth ensures penetration through the upper cohesive layer into the dense sandy murum stratum, providing improved end bearing, shaft resistance, and long-term stability.

Governing design condition: Uplift + Lateral (Wind Load governed as per IS 875 Part 3)

The recommended pile configuration provides:

- Adequate compression resistance.

- Improved uplift resistance against design wind loads.

- Satisfactory lateral load resistance.

- Reduced seasonal performance variation.

- Reliable support within the dense sandy murum bearing layer.

# 4.CALIFORNIA BEARING RATIO (CBR):

4.1 Correlation Used for CBR Estimation:

For fine-grained cohesive soils (CI–CL / CL–ML)

For granular / murum soils (SM–GM):

 CBR increases with dry density.

 CBR increases with sand and gravel content.

 Lower plasticity results in higher CBR.

 Dense murum provides improved subgrade performance.

4.2 Adopted Soil Parameters (From Soil Test Summary)	:

| Depth (m) | Soil Type | UCS (kg/cm²) | Dry Density (g/cc) |
| --- | --- | --- | --- |
| 0–1 | CI – Medium Stiff Silty Clay | 1.38 | 1.63 |
| 1–2 | SM – Dense Sandy Murum | 2.10 | 1.76 |

4.3 Sample Calculation (0–1 m Depth):

Soil: CI= Medium stiff clay 
UCS = 1.38kg/cm²

Base CBR:

Considering:

- PI ≈ 20%

- Moderate plasticity

- Seasonal softening during monsoon

- Field disturbance during construction

Reduction factor ≈ 0.90 applied

Adopted,

4.4 Sample Calculation (1–2 m Depth);

Soil: Dense Sandy Murrum 
UCS = 2.10 kg/cm²

Base CBR:

4.5 Granular Layer (1-2 m Depth):

Characteristics

- Gravel fraction = 20–30%

- Dense sand content

- Low plasticity

- High dry density

- Good drainage

- Excellent compaction characteristics

- Expected CBR Range

- 10–15 %

4.6 Depth-wise Estimated CBR Values:

| Depth (m) | Soil Type | Estimated CBR (%) |
| --- | --- | --- |
| 0–1 | CI – Medium Stiff Silty Clay | 4 |
| 1–2 | SM – Dense Sandy Murum | 12 |

4.7 Governing Design CBR

For transmission line construction tracks, equipment movement areas, and tower working platforms:

 Upper 0.5–1.0 m governs pavement performance.

 Cohesive topsoil controls subgrade behaviour.

 Dense murum layer provides improved bearing support after excavation. Conservative Design Adoption:

This accounts for:

 Seasonal moisture fluctuations in Kutch.

 Construction traffic.

 Localized soft pockets.

 Long-term settlement considerations.

4.9 Design Recommendations for Transmission Line Project

 Adopt Subgrade CBR = 5% for preliminary design of temporary access roads and crane pads.

 Compact the top 300 mm to 95% Modified Proctor Density.

 Where heavy erection equipment is expected, provide a 200–300 mm Granular Sub-Base (GSB) over compacted subgrade.

 Ensure proper surface drainage to avoid saturation around tower foundations.

 Avoid prolonged water accumulation during monsoon by providing side drains and cross-fall on temporary access tracks.

 After excavation for tower foundations, remove any loose or softened material before placing PCC or concrete.

# 5. EARTH RESISTIVITY

Basis of Estimation:

Earth resistivity (ρ) depends primarily on:

• Soil type
• Moisture content
• Bulk density
• Clay percentage
• Degree of compaction

The proposed transmission line location at Nirona, Bhuj (Kutch) generally consists of:

- Medium stiff silty clay in the upper layer

- Dense sandy murum below 1.0 m depth

- Semi-arid climatic conditions

- Low natural moisture content

- No groundwater encountered within the preliminary investigation depth (2.0 m)

These conditions generally produce moderate to moderately high earth resistivity, particularly during the dry season.

Correlation Method Used for Resistivity:

Empirical correlation widely applied in design practice:

Where:

Soil Behaviour Influence on Resistivity:

| Soil Parameter | Effect on Resistivity |
| --- | --- |
| Clay ↑ | Resistivity ↓ |
| Moisture ↑ | Resistivity ↓ |
| Sand/Murrum ↑ | Resistivity ↑ |
| Density ↑ | Resistivity ↓ |

In this project:

 Upper layer consists of cohesive silty clay (moderate resistivity)

 Lower layer consists of dense sandy murum (higher resistivity)

 Semi-arid climate causes seasonal drying

 Groundwater not encountered within 2.0 m

Adopted Soil Parameters (From Soil Summary):

| Depth (m) | Soil Type | Bulk Density (g/cc) | Moisture Condition |
| --- | --- | --- | --- |
| 0–1 | CI – Medium Stiff Silty Clay | 1.90 | Moderate |
| 1–2 | SM – Dense Sandy Murum | 2.00 | Dry to Moderate |

Sample Calculation (1–2 m Depth):

Layer: SM  (Dense sandy murum)
Bulk Density (γ) = 2.00 g/cc
Moisture Condition = Dry to Moderate
Soil Type = Dense Granular Murum

Typical empirical resistivity range for dense sandy murum under semi-arid conditions:

Considering:

 No groundwater encountered

 Semi-arid regional climate

 Dry granular soil

 Low natural moisture

Dense compacted murum Applying dry-season correction factor (+10%):

Rounded practical design range:

Estimated Resistivity by Layer:

| Depth (m) | Soil Type | Estimated Resistivity (Ω·m) |
| --- | --- | --- |
| 0–1 | CI- Medium stiff Silty Clay | 50-60 |
| 1–2 | SM- Dense Sandy Murum | 80-90 |

Seasonal Variation:

- During monsoon → Resistivity may decrease by 20–35%

- During peak summer → Resistivity increases due to drying of the upper soil layers.

- Long-term design should consider dry-season resistivity.

- Upper clay layer may crack during extreme summer, resulting in localized increase in resistivity.

Therefore, a conservative upper-bound value is adopted for design.

Final Adopted Design Resistivity:

Earth Resistivity Conclusion:

| Parameter | Value |
| --- | --- |
| Estimated Resistivity | 50-90 Ω·m |
| Adopted Design Resistivity | 85 Ω·m |
| Earthing Type | Copper-bonded GI Pipe Earthing with interconnected grounding conductor |
| Recommended Pit Depth | 3.0 m |
| Target Earth Resistance | ≤ 10 Ohm (Substation) |
| Backfill Material | Bentonite-based conductive compound (or Charcoal + Salt where specified) |
| Seasonal Variation | 20-35% reduction during monsoon |